## Lamp Qty Calc
UVC Lamp Quantity Calculation for Inline Duct Installations
How to use this spreadsheet:
1. Fill in customer supplied information. (columns B thru F)
2. Specify lamp size based upon duct size. (Enter in column H)
3. Determine lamp output from " Lamp Output" sheet. (Enter into column I) * use 12" intensity with velocity correction
4. Lamps are calculated for providing 2,500 uW dose. For other doses, change dosage in cell B22.
5. Column J will show the number of lamps recommended. If an odd number, round UP (never round down) to the next even number.
Item | Duct |  |  | CFM | Temp. (°F) | (V) FPM | Lamp size | Lamp Output (See "Lamp Output" sheet) | # lamps | duct sq. ft. | kill zone volume (cu.ft.) | dwell time (s) | Intensity required (Enter desired dosage in cell B6. Default is 2500µW) | Lamp Intensity @ Temp
| Width (inches) | Height (inches) | Length (ft.)
[6 empty] | #DIV/0! |  |  | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
[6 empty] | #DIV/0! |  |  | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
[6 empty] | #DIV/0! |  |  | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
[6 empty] | #DIV/0! |  |  | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
[6 empty] | #DIV/0! |  |  | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
[6 empty] | #DIV/0! |  |  | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
[6 empty] | #DIV/0! |  |  | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
[6 empty] | #DIV/0! |  |  | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
Dose (in µW) = | 2500
Notes: - Columns in Grey and Green will "self-fill" when the appropriate information is entered in columns as instructed above. - Do not enter anything into columns G, J, K, L, M, N or O. - The # in Column J will be the number of lamps required to achieve the one-pass dosage in cell B21. Always round UP to the nearest even number. - When the appropriate number of lamps is determined, one selects the appropriate combination of 2-lamp and 4-lamp duct units in the appropriate lamp size to acheive this total number.

## Lamp Output
Lamp Output & Corrections
Calculations based on 45 deg air temp. Temp input on sheet 1 corrects for temperature
Model # | Lamp P/N | Arc Length | UVC Watts | UVC Intensity @ 1m | UVC Intensity @ 12"
[5 empty] | 400fpm | 600 fpm | 800 fpm | 1000 fpm
DC14 | SBL405 | 11 | 8 | 99 uW/cm2 | 642 | 577.8 | 513.6 | 449.4
DC16 | SBL430 | 13 | 10 | 117 uW/cm2 | 758 | 682.2 | 606.4 | 530.6
DC24 | SBL415 | 21 | 16.2 | 189 uW/cm2 | 1225 | 1102.5 | 980 | 857.5
DC33 | SBL420 | 30.19 | 25 | 272 uW/cm2 | 1763 | 1586.7 | 1410.4 | 1234.1
DC45 | SBL445 | 42.2 | 36.1 | 380 uW/cm2 | 2462 | 2215.8 | 1969.6 | 1723.4